## Overview
|  |  |  | Projectnumber: | [Enter proj nr]
|  |  |  | Projectname: | [Enter proj name]
Sheet | Impl. PLC | Impl. HMI | Activation | HMI Test | IO Check
Valve | 0% | 0% | 0% | 0% | 0%
Motor | 0% | 0% | 0% | 0% | 0%
DI | 0% | 0% |  | 0% | 0%
DO | 0% | 0% | 0% | 0% | 0%
AI | 0% | 0% |  | 0% | 0%
AO | 0% | 0% |  | 0% | 0%
PID | 0% | 0% | 0% | 0%
Sum | 0% | 0% |  | 0% | 0%
Alarm | 0% | 0% |  | 0%
Changelog
V1.6 | • Based on the example_td from automation_boilerplate where we had added inclusive data to be generate source files to Intouch, SQL and TIA • Change alarm sheet alot to be able to generate alarms from automation_boilerplate • Cleanup, remove unneccessary data, improve look & feel • Utilize name manager in excel to decrease coupling between sheets • Update Configurations sheet, use named tables instead of hardcoded reference

## Valve
[9 empty] | Projectnumber: | [Enter proj nr]
[9 empty] | Projectname: | [Enter proj name]
Drawing | ID | Description | Alarm Group | PLC | Config | Impl. PLC | Impl. HMI | Activation | HMI Test | IO Check | Config ID | ASI Addr | ASI Master
| 57 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[6 empty] | 0% | 0% | 0% | 0% | 0%
| TL0T01V10 | Tank CIP pressure | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 1A | AS100
| TL0T01V01 | Tank Bottom Valve | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 2A | AS100
| TL0T01V02 | Tank Drain Valve | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 3A | AS100
| TL0T02V10 | Tank CIP pressure | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 4A | AS100
| TL0T02V01 | Tank Bottom Valve | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 5A | AS100
| TL0T02V02 | Tank Drain Valve | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 6A | AS100
| TL0L01V01 | Line Transfer TL0T01 | TankToTank | PLC1 | Mixproof, Act FB, DeAct FB | [5 empty] | 63 | 7A | AS100
| TL0L01V02 | Line Transfer TL0T02 | TankToTank | PLC1 | Mixproof, Act FB, DeAct FB | [5 empty] | 63 | 8A | AS100
| A50T01V10 | Tank CIP pressure | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 9A | AS100
| A50T01V01 | Tank Bottom Valve | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 1A | AS400
| A50T01V02 | Tank Drain Valve | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 2A | AS400
| A50T02V10 | Tank CIP pressure | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 3A | AS400
| A50T02V01 | Tank Bottom Valve | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 4A | AS400
| A50T02V02 | Tank Drain Valve | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 5A | AS400
| A50L01V03 | Line Transfer A50T01 | TankToTank | PLC1 | Mixproof, Act FB, DeAct FB | [5 empty] | 63 | 6A | AS400
| A50L01V04 | Line Transfer A50T02 | TankToTank | PLC1 | Mixproof, Act FB, DeAct FB | [5 empty] | 63 | 7A | AS400
| A30T01V10 | Tank CIP pressure | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 8A | AS400
| A30T01V01 | Tank Bottom Valve | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 9A | AS400
| A30T01V02 | Tank Drain Valve | TankToTank | PLC1 | Main, Act FB, DeAct FB | [5 empty] | 57 | 10A | AS400
| TL0L02V01 | Line Transfer TL0T01 | TankToTank | PLC1 | Mixproof, Act FB, DeAct FB | [5 empty] | 63 | 1A | AS500
| TL0L02V02 | Line Transfer TL0T02 | TankToTank | PLC1 | Mixproof, Act FB, DeAct FB | [5 empty] | 63 | 2A | AS500
| T1600_V1000 | Drain | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 1A | AS200
| T1600_V1001 | Outlet L1600 | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 2A | AS200
| T1600_V1005 | Water | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 3A | AS200
| T1601_V1000 | Drain | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 4A | AS200
| T1601_V1001 | Outlet L1600 | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 5A | AS200
| T1601_V1003 | Inlet L1600 | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 6A | AS200
| T1601_V1004 | Inlet L1601 | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 7A | AS200
| T1602_V1000 | Drain | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 8A | AS200
| T1602_V1001 | Outlet L1600 | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 9A | AS200
| T1602_V1003 | Inlet L1600 | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 10A | AS200
| T1602_V1005 | Water | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 11A | AS200
| T1602_V1006 | Steam | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 12A | AS200
| T1602_V1007 | Concentration | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 13A | AS200
| T1603_V1000 | Drain | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 14A | AS200
| T1603_V1001 | Outlet L1600 | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 15A | AS200
| T1603_V1003 | Inlet L1600 | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 16A | AS200
| T1603_V1005 | Water | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 17A | AS200
| T1603_V1006 | Steam | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 18A | AS200
| T1603_V1007 | Concentration | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 19A | AS200
| L1601_V1100 | Steam | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 20A | AS200
| L1601_V1101 | BTD Inlet | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 21A | AS200
| L1601_V1102 | BTD Outlet | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 22A | AS200
| L1601_V1103 | BTD Drain | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 23A | AS200
| L1601_V1104 | End Line Drain | CIP | PLC2 | Main, Act FB, DeAct FB | [5 empty] | 57 | 24A | AS200
| TL0P01V001 | Homogenisator Bypass | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 1A | AS300
| TL0P01V002 | Omslags ventil | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 2A | AS300
| TL0P01V003 | Exchange 2,3,4 Bypass | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 3A | AS300
| TL0P01V004 | Outlet valve | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 4A | AS300
| TL0P01V005 | Stopp valve | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 5A | AS300
| TL0P01V006 | Drain valve | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 6A | AS300
| TL0P01V007 | BTD Spray ball | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 7A | AS300
| TL0P01V008 | Icewater Product Cooler | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 8A | AS300
| TL0P01V009 | Hotwatter HC | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 9A | AS300
| TL0P01V010 | Hotwater Pre-Heater | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 10A | AS300
| TL0P01V011 | Water pressure | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 11A | AS300
| TL0P01V050 | Product inlet | Past | PLC3 | Main, Act FB, DeAct FB | [5 empty] | 57 | 12A | AS300
Note on B3: Valve number from P&ID
Note on C3: Process description of the function of the valve
Note on E3: What PLC is the output controlled from?
Note on G3: Is the valve object implemented in the PLC program? X = Done P = In Progress
Note on H3: Is the valve object fully implemented on the HMI? X = Done P = In Progress
Note on I3: Is the activation tested? X = Done P = In Progress
Note on J3: Check that indication, popup, alarm apppears in alarm list. X = Done P = In Progress
Note on K3: Is the valve fully IO tested? Meaning all inputs and outputs of the Valve are ok. X = Done P = In Progress
Note on L3: Constant used inside PLC, set on datablock structure. If automation boilerplate is used it will set the start-value to this value inside the sourcefile.

## Motor
[9 empty] | Projectnumber: | [Enter proj nr]
[9 empty] | Projectname: | [Enter proj name]
Drawing | ID | Description | Alarm Group | PLC | Config | Impl. PLC | Impl. HMI | Activation | HMI Test | IO Check | Config ID
| 14 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[6 empty] | 0% | 0% | 0% | 0% | 0%
| TL0T01M01 | Tank agitator | TankToTank | PLC1 | Forward, Forward FB | [5 empty] | 21
| TL0T02M01 | Tank agitator | TankToTank | PLC1 | Forward, Forward FB | [5 empty] | 21
| TL0L01M01 | Line pump | TankToTank | PLC1 | Forward, Forward FB | [5 empty] | 21
| A50T01M01 | Tank agitator | TankToTank | PLC1 | Forward, Forward FB | [5 empty] | 21
| A50T02M01 | Tank agitator | TankToTank | PLC1 | Forward, Forward FB | [5 empty] | 21
| A30T01M01 | Tank agitator | TankToTank | PLC1 | Forward, Forward FB | [5 empty] | 21
| T1602_M1000 | Caustic tank circulation | CIP | PLC2 | Forward, Forward FB | [5 empty] | 21
| T1603_M1000 | Acid tank circulation | CIP | PLC2 | Forward, Forward FB | [5 empty] | 21
| L1601_M1101 | Line Pump | CIP | PLC2 | Forward, Forward FB | [5 empty] | 21
| TL0P01P001 | BTD outlet pump | Past | PLC3 | Forward, Forward FB | [5 empty] | 21
| TL0P01P002 | Booster pump | Past | PLC3 | Forward, Forward FB | [5 empty] | 21
| TL0P01P003 | Hotwater pump HC | Past | PLC3 | Forward, Forward FB | [5 empty] | 21
| TL0P01P004 | Hotwater pump Pre-Heater | Past | PLC3 | Forward, Forward FB | [5 empty] | 21
| TL0P01P005 | Homogenisator | Past | PLC3 | Forward, Forward FB | [5 empty] | 21

## DI
[6 empty] | Projectnumber: | [Enter proj nr]
[6 empty] | Projectname: | [Enter proj name]
Drawing | ID | Description | Alarm Group | PLC | Impl. PLC | Impl. HMI | HMI Test | IO Check
| 17 |  |  |  | 0 | 0 | 0 | 0
[5 empty] | 0% | 0% | 0% | 0%
| TL0T01LSH01 | Tank High Level | TankToTank | PLC1
| TL0T01LSL01 | Tank Low Level | TankToTank | PLC1
| TL0T01GS01 | Tank Manway | TankToTank | PLC1
| TL0T02LSH01 | Tank High Level | TankToTank | PLC1
| TL0T02LSL01 | Tank Low Level | TankToTank | PLC1
| TL0T02GS01 | Tank Manway | TankToTank | PLC1
| A50T01LSH01 | Tank High Level | TankToTank | PLC1
| A50T01LSL01 | Tank Low Level | TankToTank | PLC1
| A50T01GS01 | Tank Manway | TankToTank | PLC1
| A50T02LSH01 | Tank High Level | TankToTank | PLC1
| A50T02LSL01 | Tank Low Level | TankToTank | PLC1
| A50T02GS01 | Tank Manway | TankToTank | PLC1
| A30T01LSH01 | Tank High Level | TankToTank | PLC1
| A30T01LSL01 | Tank Low Level | TankToTank | PLC1
| A30T01GS01 | Tank Manway | TankToTank | PLC1
| TL0P01GS001 | BTD Manway | Past | PLC3
| TL0P01LSH001 | BTD High Level | Past | PLC3

## DO
[7 empty] | Projectnumber: | [Enter proj nr]
[7 empty] | Projectname: | [Enter proj name]
Drawing | ID | Description | Alarm Group | PLC | Impl. PLC | Impl. HMI | Activation | HMI Test | IO Check
| 1 |  |  |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0% | 0% | 0% | 0% | 0%
| ErrorLamp | Error lamp | TankToTank | PLC1

## AI
[8 empty] | Projectnumber: |  | [Enter proj nr]
[8 empty] | Projectname: |  | [Enter proj name]
Drawing | ID | Description | Alarm Group | PLC | Impl. PLC | Impl. HMI | HMI Test | IO Check | Eng. Unit | Eng. Min | Eng. Max
| 42 |  |  |  | 0 | 0 | 0 | 0
[5 empty] | 0% | 0% | 0% | 0% |  | Min | Max
| TL0T01TT01 | Tank temperature | TankToTank | PLC1 |  |  |  |  | °C | 0 | 160
| TL0T01PT01 | Tank bottom pressure | TankToTank | PLC1 |  |  |  |  | bar | 0 | 10
| TL0T02TT01 | Tank temperature | TankToTank | PLC1 |  |  |  |  | °C | 0 | 160
| TL0T02PT01 | Tank bottom pressure | TankToTank | PLC1 |  |  |  |  | bar | 0 | 10
| A50T01TT01 | Tank temperature | TankToTank | PLC1 |  |  |  |  | °C | 0 | 160
| A50T01PT01 | Tank bottom pressure | TankToTank | PLC1 |  |  |  |  | bar | 0 | 10
| A50T02TT01 | Tank temperature | TankToTank | PLC1 |  |  |  |  | °C | 0 | 160
| A50T02PT01 | Tank bottom pressure | TankToTank | PLC1 |  |  |  |  | bar | 0 | 10
| TL0L01FT01 | Transfer line flow | TankToTank | PLC1 |  |  |  |  | l/h | 0 | 50000
| TL0L01PT01 | Transfer line pressure | TankToTank | PLC1 |  |  |  |  | bar | 0 | 10
| TL0T01LT01 | Tank Level | TankToTank | PLC1 |  |  |  |  | % | 0 | 100
| TL0T02LT01 | Tank Level | TankToTank | PLC1 |  |  |  |  | % | 0 | 100
| A50T01LT01 | Tank Level | TankToTank | PLC1 |  |  |  |  | % | 0 | 100
| A50T02LT01 | Tank Level | TankToTank | PLC1 |  |  |  |  | % | 0 | 100
| A30T01LT01 | Tank Level | TankToTank | PLC1 |  |  |  |  | % | 0 | 100
| A30T01TT01 | Tank temperature | TankToTank | PLC1 |  |  |  |  | °C | 0 | 160
| A30T01PT01 | Tank bottom pressure | TankToTank | PLC1 |  |  |  |  | bar | 0 | 10
| TL0L02FT01 | Transfer line flow | TankToTank | PLC1 |  |  |  |  | l/h | 0 | 50000
| TL0L02PT01 | Transfer line pressure | TankToTank | PLC1 |  |  |  |  | bar | 0 | 10
| T1600_LT1000 |  | CIP | PLC2 |  |  |  |  | l | 0 | 30000
| T1600_TT1001 |  | CIP | PLC2 |  |  |  |  | °C | 0 | 160
| T1601_LT1000 |  | CIP | PLC2 |  |  |  |  | l | 0 | 30000
| T1601_TT1001 |  | CIP | PLC2 |  |  |  |  | °C | 0 | 160
| T1602_LT1000 |  | CIP | PLC2 |  |  |  |  | l | 0 | 30000
| T1602_TT1001 |  | CIP | PLC2 |  |  |  |  | °C | 0 | 160
| T1602_TT1002 |  | CIP | PLC2 |  |  |  |  | °C | 0 | 160
| T1602_CT1003 |  | CIP | PLC2 |  |  |  |  | mS | 0 | 200
| T1603_LT1000 |  | CIP | PLC2 |  |  |  |  | l | 0 | 30000
| T1603_TT1001 |  | CIP | PLC2 |  |  |  |  | °C | 0 | 160
| T1603_TT1002 |  | CIP | PLC2 |  |  |  |  | °C | 0 | 160
| T1603_CT1003 |  | CIP | PLC2 |  |  |  |  | mS | 0 | 200
| L1601_TT1100 |  | CIP | PLC2 |  |  |  |  | °C | 0 | 160
| L1601_FT1101 |  | CIP | PLC2 |  |  |  |  | l/h | 0 | 50000
| L1601_TT1102 |  | CIP | PLC2 |  |  |  |  | °C | 0 | 160
| L1601_CT1103 |  | CIP | PLC2 |  |  |  |  | mS | 0 | 200
| L1601_FT1104 |  | CIP | PLC2 |  |  |  |  | l/h | 0 | 50000
| TL0P01TT001 | Product temp | Past | PLC3 |  |  |  |  | °C | 0 | 160
| TL0P01TT003 | Temp after Pre-Heater | Past | PLC3 |  |  |  |  | °C | 0 | 160
| TL0P01TT004 | Temp before HC | Past | PLC3 |  |  |  |  | °C | 0 | 160
| TL0P01TT006 | Temp after HC | Past | PLC3 |  |  |  |  | °C | 0 | 160
| TL0P01TT008 | Temp before Pre-Heater | Past | PLC3 |  |  |  |  | °C | 0 | 160
| TL0P01FT001 | Flow machine | Past | PLC3 |  |  |  |  | l/h | 0 | 30000

## AO
[9 empty] | Projectnumber: |  | [Enter proj nr]
[9 empty] | Projectname: |  | [Enter proj name]
Drawing | ID | Description | Alarm Group | PLC | Impl. PLC | Impl. HMI | Activation | HMI Test | IO Check | Eng. Unit | Eng. Min | Eng. Max
| 18 |  |  |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0% | 0% | 0% | 0% | 0% |  | Min | Max
| TL0T01M01SC | Tank agitator | TankToTank | PLC1 | [5 empty] | % | 0 | 100
| TL0T02M01SC | Tank agitator | TankToTank | PLC1 | [5 empty] | % | 0 | 100
| TL0L01M01SC | Line pump | TankToTank | PLC1 | [5 empty] | % | 0 | 100
| A50T01M01SC | Tank agitator | TankToTank | PLC1 | [5 empty] | % | 0 | 100
| A50T02M01SC | Tank agitator | TankToTank | PLC1 | [5 empty] | % | 0 | 100
| T1602_RV1000 |  | CIP | PLC2 | [5 empty] | % | 0 | 100
| T1603_RV1000 |  | CIP | PLC2 | [5 empty] | % | 0 | 100
| L1601_RV1100 |  | CIP | PLC2 | [5 empty] | % | 0 | 100
| L1601_SC1101 |  | CIP | PLC2 | [5 empty] | % | 0 | 100
| TL0P01CV001 | BTD Product inlett | Past | PLC3 | [5 empty] | % | 0 | 100
| TL0P01CV002 | Mixin valve | Past | PLC3 | [5 empty] | % | 0 | 100
| TL0P01CV003 | Machine pressure | Past | PLC3 | [5 empty] | bar | 0 | 10
| TL0P01CV005 | Icewater valve | Past | PLC3 | [5 empty] | % | 0 | 100
| TL0P01CV006 | Hotwater HC | Past | PLC3 | [5 empty] | % | 0 | 100
| TL0P01CV008 | Hotwater Pre-Heater | Past | PLC3 | [5 empty] | % | 0 | 100
| TL0P01SC001 | VLT BTD Pump | Past | PLC3 | [5 empty] | % | 0 | 100
| TL0P01SC002 | VLT Booster pump | Past | PLC3 | [5 empty] | % | 0 | 100
| TL0P01SC005 | VLT Homogenisator | Past | PLC3 | [5 empty] | % | 0 | 100

## PID
[10 empty] | Projectnumber: |  | [Enter proj nr]
[10 empty] | Projectname: |  | [Enter proj name]
Drawing | ID | Description | Alarm Group | PLC | Impl. PLC | Impl. HMI | Activation | HMI Test | Site Test | Eng. Unit | Eng. Min | Eng. Max | Parameters
| 12 |  |  |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0% | 0% | 0% | 0% | 0% |  | Min | Max | P | I | D
| TL0L01FC01 | Flow controller | TankToTank | PLC1 | [5 empty] | l/h | 0 | 50000
| A50L01FC01 | Flow controller | TankToTank | PLC1 | [5 empty] | l/h | 0 | 50000
| L1601_FC1101 |  | CIP | PLC2 | [5 empty] | l/h | 0 | 50000
| L1601_TC1100 |  | CIP | PLC2 | [5 empty] | °C | 0 | 160
| T1602_TC1002 |  | CIP | PLC2 | [5 empty] | °C | 0 | 160
| T1603_TC1002 |  | CIP | PLC2 | [5 empty] | °C | 0 | 160
| TL0P01LC001 | BTD Level | Past | PLC3 | [5 empty] | % | 0 | 100
| TL0P01TC001 | Product outlet temperature | Past | PLC3 | [5 empty] | °C | 0 | 160
| TL0P01TC003 | Product pre-heat | Past | PLC3 | [5 empty] | °C | 0 | 160
| TL0P01TC004 | HC Temperature | Past | PLC3 | [5 empty] | °C | 0 | 160
| TL0P01PC002 | Product pressure to Homo | Past | PLC3 | [5 empty] | bar | 0 | 10
| TL0P01FC001 | Flow controller | Past | PLC3 | [5 empty] | l/h | 0 | 30000

## Sum
[9 empty] | Projectnumber: |  | [Enter proj nr]
[9 empty] | Projectname: |  | [Enter proj name]
Drawing | ID | Description | Alarm Group | PLC | Impl. PLC | Impl. HMI | HMI Test | IO Check | Eng. Unit | Eng. Min | Eng. Max | Volume Per Pulse
| 7 |  |  |  | 0 | 0 | 0 | 0
[5 empty] | 0% | 0% | 0% | 0%
| TL0L01FT01_Sum | Flow totalizer | TankToTank | PLC1 |  |  |  |  | l | 0 | 999999 | 10
| A50L01FT01_Sum | Flow totalizer | TankToTank | PLC1 |  |  |  |  | l | 0 | 999999 | 10
| TL0L02FT01_Sum | Flow totalizer | TankToTank | PLC1 |  |  |  |  | l | 0 | 999999 | 10
| A30L01FT01_Sum | Flow totalizer | TankToTank | PLC1 |  |  |  |  | l | 0 | 999999 | 10
| L1601_FT1101_Sum | Flow totalizer | CIP | PLC2 |  |  |  |  | l | 0 | 999999 | 10
| L1601_FT1104_Sum | Flow totalizer | CIP | PLC2 |  |  |  |  | l | 0 | 999999 | 10
| TL0P01FT001Sum | Flow totalizer | Past | PLC3 |  |  |  |  | l | 0 | 999999 | 10

## Phases
[12 empty] | Projectnumber: |  | [Enter proj nr]
[12 empty] | Projectname: |  | [Enter proj name]
| Added in PLC |  |  |  |  | Added in HMI | Added in HMI | Added in HMI | Added in HMI | Added in HMI | Office Test | Office Test | Office Test | Office Test | Site Test
| Phase | IL/ RF | Activations | Alarm | Step Seq | Tag list | Start/stop | Indication | Que | menue | Func | Alarm | Valve act | IL/RF
Pasteurizer
Sterilisation
Water Circulation
Production
CIP
T1001
Agitation
Cooling
Cleaning
Service
Filling
Emptying

## Alarm
[8 empty] | Projectnumber: | [Enter proj nr]
[8 empty] | Projectname: | [Enter proj name]
ID | Description | Alarm Text | Alarm Group | PLC | Alarm Prio | Impl. PLC | Impl. HMI | Test | Alarm Prio ID
10 | [5 empty] | 0 | 0 | 0 | Color that will be displayed in alarmlist
[6 empty] | 0% | 0% | 0%
CommFault_TankToTank_CIP |  | PLC Communication fault CIP Station <> TankToTank | TankToTank | PLC1 | Critical alarm |  |  |  | 1
CommFault_TankToTank_Past |  | PLC Communication fault TankToTank <> Pasteurizer | TankToTank | PLC1 | Critical alarm |  |  |  | 1
L1601_HighConcReturn |  | L1601 - High Concentration Return | CIP | PLC2 | Alarm |  |  |  | 250
L1601_LowConcReturn |  | L1601 - Low Concentration Return | CIP | PLC2 | Alarm |  |  |  | 250
L1601_HighTempPressure |  | L1601 - High Temperature Pressure | CIP | PLC2 | Alarm |  |  |  | 250
L1601_HighTempReturn |  | L1601 - High Temperature Return | CIP | PLC2 | Alarm |  |  |  | 250
L1601_LowTempReturn |  | L1601 - Low Temperature Return | CIP | PLC2 | Alarm |  |  |  | 250
L1601_HighPressureReturn |  | L1601 - High Pressure Return | CIP | PLC2 | Alarm |  |  |  | 250
CommFault_Past_CIP |  | PLC Communication fault CIP Station <> Pasteurizer | Past | PLC3 | Critical alarm |  |  |  | 1
EMStop_Past |  | Emergency Stop Pasteurizer | Past | PLC3 | Critical alarm |  |  |  | 1
Note on A3: Eddie Karlsson: Alarm Taggnamn, Måste vara med understeck som avskiljare, inga mellanslag eller bindestreck!
Note on J3: Constant value used set on HMI alarm tag & color in HMI alarm list

## _configs
Legal binary Valve configurations |  | Legal binary Motor configurations |  | Legal Alarm priorities
Description | Value | Description | Value | Description | Value
None | 0 | None | 0 | Critical alarm | 1
Main | 33 | Forward | 17 | Alarm | 250
Main, Act FB | 37 | Forward, Forward FB | 21 | Warning | 500
Main, DeAct FB | 47 | Forward, Forward FB, Circuit Breaker | 85 | Message | 750
Main, Act FB, DeAct FB | 57
Mixproof, Act FB, DeAct FB | 63
Main, Disable manmode | 97
Main, Act FB, Disable manmode | 101
Main, DeAct FB, Disable manmode | 111
Main, two FB, Disable manmode | 121
Mixproof, two FB, Disable manmode | 127